{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Effektbudsjett "],"not_rendered":{"charts":1,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Effektbudsjett ","index":0,"n_rows":36,"n_cols":16,"rows_kept":36,"cut":false,"hidden":false,"merged":[[28,7,29,10],[26,7,27,10],[26,3,29,3],[24,6,25,6],[13,3,14,3],[2,11,2,12],[2,14,2,15],[13,4,13,5],[9,3,12,5]]}
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,"2x10A",0,null,"2x10A",0]
[null,null,null,null,null,null,null,null,null,null,null,"2x16A",2.4,null,"2x16A",2.4]
[null,null,null,null,null,null,null,null,null,null,null,"2x20A",3.69,null,"2x20A",3.69]
[null,null,null,null,null,null,null,null,null,null,null,"2x25A",4.7,null,"2x25A",4.7]
[null,null,null,"Effektbudsjett for elektriske anlegg",null,null,null,null,null,null,null,"2x32A",5.76,null,"2x32A",5.76]
[null,null,null,null,null,null,null,null,null,null,null,"2x40A",7.37,null,"2x40A",7.37]
[null,null,null,null,null,null,null,null,null,null,null,"2x50A",9.3000000000000007,null,"2x50A",9.3000000000000007]
[null,null,null,null,null,null,null,null,null,null,null,"2x56A",11.3,null,"2x56A",11.3]
[null,null,null,"Energibærer","Elektrisk installert effekt",null,"Samtidighets effekt",null,null,"Typiske verdier pr. bygningstype",null,"2x63A",13,null,"2x63A",13]
[null,null,null,null,"Samtidighet","Effekt i kW","Effekt i kW",null,null,"Bruksområde                                    ","Samtidighetsfaktor","2x80A",14.6,null,"2x80A",14.6]
[null,null,null,"Elektrisk oppvarming",null,null,{"$f":"E16*F16","v":0},"kW",null,null,null,"Ikke tilgjengelig",18.5,null,"Ikke tilgjengelig",18.5]
[null,null,null,"Oppvarming av tappevann",null,null,0,"kW",null,"Små kontorer                                                            ","0,5-0,7"]
[null,null,null,"Ventilasjon",null,null,0,"kW",null,"Store kontorer, banker ol.                             ","0,7-0,8","4x10A",0,null,"3x10A",0]
[null,null,null,"Belysning",null,null,0,"kW",null,"Butikker                                                                     ","0,5-0,7","4x16A",6.94,null,"3x16A",3.99]
[null,null,null,"Tekniske anlegg",null,null,0,"kW",null,"Varehus                                                                      ","0,7-0,9","4x20A",11.09,null,"3x20A",6.38]
[null,null,null,"Ladeanlegg for elbil",null,null,0,"kW",null,"Skoler                                                                          ","0,6-0,7  ","4x25A",13.95,null,"3x25A",7.97]
[null,null,null,"Diverse",null,null,{"$f":"E22*F22","v":0},"kW",null,"Boliger med el. oppvarming                               ","0,4-0,7","4x32A",17.420000000000002,null,"3x32A",9.9]
[null,null,null,null,null,null,null,null,null,"Boliger med el. oppvarming & el.lader           ","0,5-0,75","4x40A",22.3,null,"3x40A",12.8]
[null,null,null,"Installasjonens dimmensjonerende effekt",{"$f":"IFERROR(AVERAGEIF(E16:E22,\">0\",E16:E22),\"0\")","v":"0"},{"$f":"F16+F17+F18+F19+F20+F21+F22","v":0},{"$f":"E24*F24","v":0},"kW",null,null,null,"4x50A",27.7,null,"3x50A",16.100000000000001]
[null,null,null,null,null,null,"Beregnet vern ",null,null,null,null,"4x56A",34.6,null,"3x56A",20.100000000000001]
[null,null,null,"Kommentarfelt",null,null,null,null,null,null,null,"4x63A",38.799999999999997,null,"3x63A",22.4]
[null,null,null,null,"1-Fase","TN 400V",{"$f":"LOOKUP(G24,M6:M16,L6:L16)","v":"2x10A"},null,null,null,null,"4x80A",43.7,null,"3x80A",25.2]
[null,null,null,null,"3-Fase","TN 400V",{"$f":"LOOKUP(G24,M18:M36,L18:L36)","v":"4x10A"},null,null,null,null,"4x100A",55.5,null,"3x100A",32]
[null,null,null,null,"2-Fase","IT 230V",{"$f":"LOOKUP(G24,P6:P16,O6:O16)","v":"2x10A"},null,null,null,null,"4x125A",69.290000000000006,null,"3x125A",39.9]
[null,null,null,null,"3-Fase","IT 230V",{"$f":"LOOKUP(G24,P18:P36,O18:O36)","v":"3x10A"},null,null,null,null,"4x160A",86.6,null,"3x160A",49.9]
[null,null,null,null,null,null,null,null,null,null,null,"4x200A",110.86,null,"3x200A",63.8]
[null,null,null,null,null,null,null,null,null,null,null,"4x250A",138.57,null,"3x250A",79.7]
[null,null,null,null,null,null,null,null,null,null,null,"4x300A",173.3,null,"3x300A",99.7]
[null,null,null,null,null,null,null,null,null,null,null,"4x350A",207.85,null,"3x350A",119.6]
[null,null,null,null,null,null,null,null,null,null,null,"4x400A",207.85,null,"3x400A",139.5]
[null,null,null,null,null,null,null,null,null,null,null,"Ikke tilgjengelig",277.13,null,"Ikke tilgjengelig",159.19999999999999]